z1Power · STR MEDICAL

REQUEST FOR INFORMATION RFI-001

Project: z1Power Sugarland BESS — 375 kW / 1,221 kWh, ERCOT — Combined EMS+MBMU control enclosure, DWG Z1SL-E-001 / Z1SL-A3-000 Rev K

To: Kehua Tech — applications engineering, Cabinet-375 BESS PCS

From: STR Medical / z1Power engineering — yasir@futonix.com

Date: 2026-08-09        Response requested within: 10 business days        Priority: fabrication-gating

Subject: Cabinet-375 integrated PCS — aux transformer, output protection, EPO, and Modbus interface

| # | QUESTION | WHY IT GATES THE DESIGN |
| --- | --- | --- |
| 1 | Confirm the built-in 30 kVA aux transformer secondary configuration: 380Y/220 V with distributed neutral? Neutral conductor ampacity and whether the neutral lands on an output breaker. | Panel aux distribution (Q2/TB13, CB3-CB11) assumes 380Y/220 with full neutral. |
| 2 | Ampere rating, pole count, trip curve, and interrupting rating of EACH of the three aux output breakers. | Feeder is an NEC 240.21(B)(2) tap sized to 1/3 of your breaker: >30 A forces a feeder upsize from AWG10 (drawing note, sheet 4). |
| 3 | Location of the aux system N-G bond and grounding-electrode connection — inside the Cabinet-375? Confirm the panel must NOT bond neutral to ground (we bond only the 120 V CPT). | NEC 250.30 one-bond rule — board finding R-07 removed a stale double-bond instruction; your answer closes it permanently. |
| 4 | EPO / remote-stop input: terminal designations, contact sense (open-to-stop or close-to-stop), wetting voltage/current, response time, and latching behavior. Our fire panel provides BOTH senses via relay K1 at interface X23 (Rev K). | Board finding R-01: hardwired fire→PCS trip. We wire the pair you specify and park the other. |
| 5 | PCS self-consumption from the aux bus (standby + operating) for the 30 kVA loading census. | Aux transformer loading calc, schedule Z1SL-SCH-001. |
| 6 | Modbus TCP: protocol revision covering the BCS125K modules inside Cabinet-375, register map, number of northbound Ethernet endpoints (one per module or one per cabinet?), and master-timeout / loss-of-comms behavior (does the PCS hold, derate, or trip?). | EMS integration (CPU1/2 via SW1 P10-P12) and the fail-safe analysis both depend on timeout behavior. |
| 7 | Confirm the PCS behavior on EPO assertion vs Modbus stop: does EPO open the DC contactors, gate-block only, or both? Restart procedure after EPO? | Emergency-operations plan interface required by NFPA 855 / AHJ. |

Responses become part of the interface control documentation for this project and will be incorporated into the Rev L drawing set. Where a response contradicts a published document, please identify the governing revision.

PROPRIETARY — STR MEDICAL · FOR REVIEW ONLY — design is not released for construction · PE review required