z1Power · STR MEDICAL

REQUEST FOR INFORMATION RFI-002

Project: z1Power Sugarland BESS — 375 kW / 1,221 kWh, ERCOT — Combined EMS+MBMU control enclosure, DWG Z1SL-E-001 / Z1SL-A3-000 Rev K

To: CATL ESS applications (EnerOne+ R08306P05L31) + Potter Electric Signal (releasing systems)

From: STR Medical / z1Power engineering — yasir@futonix.com

Date: 2026-08-09        Response requested within: 10 business days        Priority: fabrication-gating

Subject: EnerOne+ rack interfaces — aerosol releasing circuits, chiller nameplate, 24 V loads, connectors

| # | QUESTION | WHY IT GATES THE DESIGN |
| --- | --- | --- |
| 1 | JX1_IN pinout, project revision: confirm pin functions for (a) Loop_Input_24V± — manual306 table says pins 1/2, External Wiring V1.2 checklist says K/L; and (b) Aerosol Input± pins 3/4. Rev K wires FACP-supervised releasing circuits to the AEROSOL input (Option B) — confirm pins, polarity, minimum actuation voltage/current, and standby supervision current the initiator tolerates. | The entire Option B releasing chain (PSN1 → DS1 → TB14 → JX1) lands on these pins. EOL supervision current must not fire or degrade the initiator. |
| 2 | Confirm Option A (rack-native loop release on dual-detector) is fully disabled when the loop input is left unwired, and that aerosol actuation authority transfers cleanly to the external 24 V aerosol input. | Rev K leaves MBMU J3.6/23 unwired with no-connects; both architectures must never be active together. |
| 3 | Potter: confirm ARC-100 + PSN-1000 listed compatibility for this application (releasing device = CATL aerosol initiator), PSN-1000 trigger configuration from ARC-100 releasing circuits, and the listed supervised service-disconnect device you recommend for DS1. | Board findings R-12/R-15; DS1 is currently specified generically pending your listed device. |
| 4 | Chiller nameplate: RLA, MCA, MOCP, and locked-rotor current for the EnerOne+ chiller. Published figures conflict (3 kW / '10 A' / 12.5 A inrush spec / 31 A EW surge). | NEC Art. 440 branch sizing — CB3/5/7 final value (currently 20 A C-curve) and the 440.22(A) ceiling. |
| 5 | MBMU and ETH-module 24 VDC quiescent and peak currents. | 24 V load schedule + fuse values F13-F17 (currently KLKR-2 on catalog-family estimates). |
| 6 | JX1_IN / JX2_OUT connector: full 12-position pinout for this project rev (and the 12P vs 16P housing question), contact wire-gauge range, and confirmation the SLC pass-through pins C/D support rack-to-rack Class A daisy-chaining as drawn (panel send → cab1 → cab2 → cab3 → panel return). | Rev K re-drew the SLC to your native chain (board finding R-11). |
| 7 | Terminal resistor at the rack end of MCAN: part number, who supplies it, and the expected end-to-end resistance at J902.21/22 (we expect ~60 Ω; if ~30 Ω the crimped 60R is removed). | Commissioning disposition for R1-R3 (standing ICD item). |
| 8 | Fire alarm secondary power: manual306 line 809 requires '24h power supply for fire alarm and 2h for sound and light.' Confirm whether the 2 h term applies to the panel FACP notification circuit or to rack-internal devices only. | NFPA 72 worksheet NFPA72-W1: 8 Ah installed passes a 5-min term, fails a 2 h term (13.8 Ah). |
| 9 | Cable checklist rows for aux (AWG10), CAN, and fire circuits cite withstand/spec values that appear copied from the HV harness row. Confirm the actual insulation ratings required. | Closes the cable-spec conformance rows in the commissioning package. |

Responses become part of the interface control documentation for this project and will be incorporated into the Rev L drawing set. Where a response contradicts a published document, please identify the governing revision.

PROPRIETARY — STR MEDICAL · FOR REVIEW ONLY — design is not released for construction · PE review required