## FUSE-BKR
FUSE + BREAKER SCHEDULE (REV K, board finding R-05)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
Ref | Circuit | Part number | Class / curve | Amps | Volts | IR | Mfr | Basis / notes
F1 | Meter tap L1 | KLKR-1 | Class CC fast | 1 | 600 | 200kA | Littelfuse | PT metering tap; 14AWG lead
F2 | Meter tap L2 | KLKR-1 | Class CC fast | 1 | 600 | 200kA | Littelfuse
F3 | Meter tap L3 | KLKR-1 | Class CC fast | 1 | 600 | 200kA | Littelfuse
F4 | T2 CPT primary L1 | FNQ-R-3 | Class CC time-delay | 3 | 600 | 200kA | Littelfuse | NEC 450.3(B) primary-only: <=300% x 1.04A FLA; T-D holds 12-25x magnetizing inrush
F5 | T2 CPT primary L2 | FNQ-R-3 | Class CC time-delay | 3 | 600 | 200kA | Littelfuse | matched pair with F4
F6 | PSU1 120V input | CCMR-4 | Class CC time-delay | 4 | 600 | 200kA | Littelfuse | NDR-75 input 1.6A@115V; T-D for SMPS inrush
F7 | PSU2 120V input | CCMR-4 | Class CC time-delay | 4 | 600 | 200kA | Littelfuse
F9 | PSU3 120V input | CCMR-6 | Class CC time-delay | 6 | 600 | 200kA | Littelfuse | NDR-240 input 2.2A@115V typ; inrush ~65A/2ms
F19 | PSU4 120V input | CCMR-6 | Class CC time-delay | 6 | 600 | 200kA | Littelfuse | REV K
F10 | EMS CPU1 24V | KLKR-2 | Class CC fast | 2 | 600 | 200kA | Littelfuse | UC-2222A ~0.5A
F11 | EMS CPU2 24V | KLKR-2 | Class CC fast | 2 | 600 | 200kA | Littelfuse
F12 | Network (SW1) 24V | KLKR-3 | Class CC fast | 3 | 600 | 200kA | Littelfuse | EDS-4014 ~1.2A max
F13 | MBMU1 24V | KLKR-2 | Class CC fast | 2 | 600 | 200kA | Littelfuse | MBMU quiescent [CONFIRM AT RFI-002]; FSS load now on PSN1, not this branch (REV K)
F14 | MBMU2 24V | KLKR-2 | Class CC fast | 2 | 600 | 200kA | Littelfuse
F15 | MBMU3 24V | KLKR-2 | Class CC fast | 2 | 600 | 200kA | Littelfuse
F16 | IO1 24V (UPS-backed) | KLKR-2 | Class CC fast | 2 | 600 | 200kA | Littelfuse | REV K: moved to 24V_UPS - fire-path I/O rides through AC loss
F17 | ETH modules 24V | KLKR-2 | Class CC fast | 2 | 600 | 200kA | Littelfuse | 3x EM ~0.2A each
F18 | Fire trip loop (K1 coil) | KLKR-1 | Class CC fast | 1 | 600 | 200kA | Littelfuse | REV K R-01; coil ~30mA - fuse protects wiring only
Coordination basis: supply current-limit (NDR-240 hiccup ~110% rated) clears any 24V branch fault only through the
fuse - KLKR-2 at 10x opens <0.1s at 20A fault; PSU folds back at ~11A, so branch fuses must be <= 1/3 of rail
capacity. Full TCC overlay to be produced by the panel shop at UL 508A submittal. [PROPOSED VALUES - PE TO CONFIRM]

## BREAKERS
PROTECTIVE DEVICE SPECIFICATION (REV K, board findings R-04/R-31)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
Ref | Circuit | Rating | Part number | Voltage | IR | Code basis / notes
Q1 | 480V main disconnect | 40A 3P | Phoenix TMC S3D [VERIFY] | 480V | [AIC per SCCR study] | NEC 409.20 conductor 8AWG
CB1 | SPD breaker | 30A 3P K | ABB SU203M-K30 [PROPOSED] | 480Y/277V | 10kA | per SPD instructions
CB2 | 120V control main | 15A 2P C | ABB SU202M-C15 [PROPOSED] | 240V | 10kA | shared SEC_N = MWBC, common trip required
CB9 | FIRE ALARM branch | 15A 1P C | ABB SU201M-C15 + red handle + lock-on [PROPOSED] | 240V | 10kA | NEC 760.121(B) - feeds FACP1+PSN1 ONLY; placard at FACP (REV K R-02)
Q2 | Aux main (380Y) | 25A 3P C | ABB SU203M-C25 [PROPOSED] | 480Y/277V | 10kA | UL508A incoming disc #2; two-source label
CB3/5/7 | Chiller branches | 20A 1P C | ABB SU201M-C20 [PROPOSED] | 480Y/277V | 10kA | Art. 440: final value pends CATL RLA/MCA (RFI-002); AWG10 branch
CB4/6/8 | BMS branches | 6A 1P C | ABB SU201M-C6 [PROPOSED] | 480Y/277V | 10kA | 135W/2.3A + 6A<1s inrush; 14AWG branch
CB10 | Enclosure A/C | 10A 1P C | ABB SU201M-C10 + lock [PROPOSED] | 480Y/277V | 10kA | NEC 440.14 disconnect; final per unit MCA/MOCP (REV K R-03)
CB11 | Enclosure heater | 6A 1P C | ABB SU201M-C6 [PROPOSED] | 480Y/277V | 10kA | 100W + thermostat
All UL 489. 380Y/220V system devices are 480Y/277V-rated for L-L clearing duty per NEC 240.85.
kAIC values feed the UL 508A SB4 SCCR worksheet (tab SCCR). [PROPOSED - CONFIRM AT PROCUREMENT + PE REVIEW]

## LABELS
LABEL + NAMEPLATE SCHEDULE (REV K, board finding R-17)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
ID | Purpose | Verbatim text / content | Material | Location
L-01 | 409.110 nameplate | Z1POWER / STR MEDICAL - INDUSTRIAL CONTROL PANEL Z1SL-E-001 REV K - 480V 3PH 60HZ FLA 1.3A (SUPPLY 1) / 380Y-220V 3PH 60HZ FLA 17.9A (SUPPLY 2) - WIRING DIAG Z1SL-E-001 - ENCLOSURE TYPE 4 - SCCR ___ kA (SB4 WORKSHEET) | Engraved phenolic | Front door, upper left
L-02 | 409.22(B) fault current | AVAILABLE FAULT CURRENT ___ A AT ___ (DATE) - PER UTILITY/EOR STUDY | Engraved phenolic | Adjacent L-01
L-03 | 110.16 arc flash | WARNING - ARC FLASH AND SHOCK HAZARD - APPROPRIATE PPE REQUIRED - incident-energy study by site EOR | ANSI Z535 vinyl | Front door center
L-04 | Two sources | WARNING - THIS PANEL IS FED FROM TWO SOURCES: 480V (Q1) AND 380Y/220V FROM PCS CABINET (Q2). DE-ENERGIZE BOTH BEFORE SERVICING (NEC 409.110) | ANSI Z535 vinyl | Front door + inner deadfront
L-05 | Fire alarm circuit | FIRE ALARM CIRCUIT (red) at CB9 + red breaker handle + lock-on | Red phenolic | At CB9
L-06 | FACP OCPD placard | FIRE ALARM POWER: CB9, THIS PANEL, CIRCUIT SEC-L1 (NEC 760.121(B)(3)/(4)) | Phenolic | At FACP1
L-07 | Stranded energy | CAUTION - LINE TERMINALS OF Q1/Q2 REMAIN ENERGIZED WHEN OPEN; FACP CONTINUES ON BATTERY | Vinyl | Inner deadfront
L-08 | 480V warnings | 480 VOLTS (orange) | Vinyl | All 480V wireways/covers
L-09 | ESS signage interface | ENERGY STORAGE SYSTEM - EMERGENCY SHUTDOWN AT THIS PANEL (K1/X23 EPO) - per NFPA 855 / IFC 1207.5.4 site signage package (by site EPC) | ANSI Z535 | Front door lower
L-10 | Releasing service disc | AEROSOL RELEASING SERVICE DISCONNECT DS1 - LOCK OPEN BEFORE CABINET ENTRY - SUPERVISED | Red phenolic | At DS1
L-11 | Abort/man-rel stations | ABORT (constant pressure) / MANUAL RELEASE station labels per NFPA 72 | Per device | Field stations X24/X25
L-12 | N-G bond | NEUTRAL-GROUND BOND (CPT ONLY) - DO NOT BOND AUX NEUTRAL IN THIS PANEL | Phenolic | At BD1 + TB13
Blanks (SCCR, fault current) are filled from the SB4 worksheet and the utility study before fabrication.

## TERMINALS
TERMINAL BLOCK SCHEDULE (generated from golden_nets.json - REV K)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
Block | Pole | Net | Terminal type note
TB1 | 1 | 480_L1 | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB1 | 2 | 480_L2 | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB1 | 3 | 480_L3 | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB1 | 4 | 480_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB1 | 5 | PE | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB2 | 1 | C1_HVAC_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB2 | 2 | AUX_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB2 | 3 | C1_BMS_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB2 | 4 | AUX_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB2 | 5 | PE | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB3 | 1 | C2_HVAC_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB3 | 2 | AUX_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB3 | 3 | C2_BMS_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB3 | 4 | AUX_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB3 | 5 | PE | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB4 | 1 | C3_HVAC_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB4 | 2 | AUX_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB4 | 3 | C3_BMS_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB4 | 4 | AUX_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB4 | 5 | PE | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB5 | 1 | CAN1_H | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB5 | 2 | CAN1_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB5 | 3 | CAN1_SHD | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB6 | 1 | CAN2_H | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB6 | 2 | CAN2_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB6 | 3 | CAN2_SHD | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB7 | 1 | CAN3_H | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB7 | 2 | CAN3_L | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB7 | 3 | CAN3_SHD | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB8 | 1 | SLC_S1P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB8 | 2 | SLC_S1N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB9 | 1 | SLC_R3P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB9 | 2 | SLC_R3N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 1 | CT_POI_1P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 2 | CT_POI_1M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 3 | CT_POI_2P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 4 | CT_POI_2M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 5 | CT_POI_3P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 6 | CT_POI_3M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 7 | CT_SOL_1P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 8 | CT_SOL_1M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 9 | CT_SOL_2P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 10 | CT_SOL_2M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 11 | CT_SOL_3P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 12 | CT_SOL_3M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 13 | CT_BESS_1P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 14 | CT_BESS_1M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 15 | CT_BESS_2P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 16 | CT_BESS_2M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 17 | CT_BESS_3P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB11 | 18 | CT_BESS_3M | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB13 | 1 | AUXF_L1 | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB13 | 2 | AUXF_L2 | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB13 | 3 | AUXF_L3 | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB13 | 4 | AUX_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB13 | 5 | PE | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB14 | 1 | SUP1_P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB14 | 2 | SUP1_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB14 | 3 | SUP2_P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB14 | 4 | SUP2_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB14 | 5 | SUP3_P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB14 | 6 | SUP3_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB15 | 1 | ABORT_P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB15 | 2 | ABORT_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB16 | 1 | MREL_P | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB16 | 2 | MREL_N | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB23 | 1 | EPO_1A | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB23 | 2 | EPO_1B | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB23 | 3 | EPO_2A | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
TB23 | 4 | EPO_2B | feed-through UK 5 N / UT series per BOM; USLKG ONLY at SB1-3
70 terminal poles across 15 blocks. Wire numbers assigned at fab release (= net name unless renumbered).

## CABLES
FIELD CABLE SCHEDULE (interfaces generated from netlist - REV K)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
Interface | Function | Nets | Cable spec | Notes
X1 | 480V feeder | 480_L1, 480_L2, 480_L3, 480_N, PE | 8AWG THHN Cu + 8AWG EGC, conduit | by site EPC
X2 | WAN uplink | ETH_WAN_UPLINK | Cat 6A shielded
X3 | PCS1 Modbus | ETH_PCS1 | Cat 6A shielded
X4 | PCS2 Modbus | ETH_PCS2 | Cat 6A shielded
X5 | PCS3 Modbus | ETH_PCS3 | Cat 6A shielded
X6 | Cab1 aux (chiller+BMS) | AUX_N, C1_BMS_L, C1_HVAC_L, PE | CATL AWG10 JONHON adapters at JXH1 | CATL supplied
X7 | Cab2 aux | AUX_N, C2_BMS_L, C2_HVAC_L, PE | CATL AWG10 JONHON adapters
X8 | Cab3 aux | AUX_N, C3_BMS_L, C3_HVAC_L, PE | CATL AWG10 JONHON adapters
X9 | Cab1 MCAN | CAN1_H, CAN1_L, CAN1_SHD | AWG20 0.5mm2 TP shielded, 20-30mm twist | single-point shield gnd at SB1
X10 | Cab2 MCAN | CAN2_H, CAN2_L, CAN2_SHD | AWG20 TP shielded | SB2
X11 | Cab3 MCAN | CAN3_H, CAN3_L, CAN3_SHD | AWG20 TP shielded | SB3
X12 | Cab1 SLC send + aerosol | SLC_S1N, SLC_S1P, SUP1_N, SUP1_P | FPL 14-18AWG (SLC) / FPL 14AWG (releasing) | R5 EOL at JX1
X13 | Cab2 aerosol | SUP2_N, SUP2_P | FPL 14AWG | R6 EOL at JX1; SLC chains rack-to-rack
X14 | Cab3 SLC return + aerosol | SLC_R3N, SLC_R3P, SUP3_N, SUP3_P | FPL 14-18AWG / FPL 14AWG | R7 EOL; return leg SEPARATE raceway
X15 | PoI CTs | CT_POI_1M, CT_POI_1P, CT_POI_2M, CT_POI_2P, CT_POI_3M, CT_POI_3P | 18AWG twisted, 333mV
X16 | Solar CTs | CT_SOL_1M, CT_SOL_1P, CT_SOL_2M, CT_SOL_2P, CT_SOL_3M, CT_SOL_3P | 18AWG twisted
X17 | BESS CTs | CT_BESS_1M, CT_BESS_1P, CT_BESS_2M, CT_BESS_2P, CT_BESS_3M, CT_BESS_3P | 18AWG twisted
X18 | 380Y/220V aux feeder from Kehua | AUXF_L1, AUXF_L2, AUXF_L3, AUX_N, PE | AWG10 Cu tap (240.21(B)(2), <=25ft) + EGC | upsize if Kehua bkr >30A - RFI-001
X23 | Kehua EPO/remote stop | EPO_1A, EPO_1B, EPO_2A, EPO_2B | 18AWG TP shielded | REV K R-01; contact sense per RFI-001
X24 | Abort station | ABORT_N, ABORT_P | FPL 14-18AWG | R8 EOL at station
X25 | Manual release station | MREL_N, MREL_P | FPL 14-18AWG | R11 EOL at station
Inter-cabinet SLC legs (cab1>cab2>cab3) are rack-to-rack field wiring by the fire contractor - FPL, separate
raceway for the return leg (Class A). Conduit fill/routing by site EPC.

## 24V-LOADS
24VDC LOAD SCHEDULE (REV K, board finding R-22)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
Load | Net | Amps | Basis | Notes
Rail A (24V_BUS > UPS1)
CPU1 UC-2222A | 24V_EMS_A | 0.5 | datasheet typ | UPS-backed
CPU2 UC-2222A | 24V_EMS_B | 0.5 | datasheet typ | UPS-backed
SW1 EDS-4014 | 24V_NET | 1.1 | datasheet max | UPS-backed
IO1 E1214 | 24V_IO | 0.2 | datasheet | UPS-backed (REV K move)
K1 coil | FT_A/FT_B | 0.03 | relay coil | UPS-backed (REV K)
RAIL A TOTAL |  | 2.33 | vs PSU1/PSU2 3.2A each via RM1 | 27% headroom single-supply; UPS1 hold-up ~70s at 56W
Rail B (24V_RMS via RM2)
MBMU1-3 | 24V_BMS1-3 | 1.5 | 0.5A ea [CONFIRM RFI-002] | telemetry
EM1-3 | 24V_ETH | 0.6 | 0.2A ea [CONFIRM RFI-002]
RAIL B TOTAL |  | 2.1 | vs PSU3/PSU4 10A each via RM2 | 79% headroom single-supply (REV K R-08)
Releasing (PSN1, separate)
Aerosol circuits x3 (alarm) | SUP1-3 | 3.41 | 1.1375A ea per CATL | PSN-1000 10A, 3A/ckt; own batteries
Device currents marked [CONFIRM] are catalog-family values pending vendor confirmation at RFI-002;
the schedule structure and headroom conclusions do not change unless a confirmed value exceeds 2x the estimate.

## T2-CENSUS
T2 CPT PER-LEG VA CENSUS (REV K, board findings R-03/R-62)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
Item | VA | Basis | Margin
Leg L1 (CTRL_L1)
PSU1 (F6) | 75 | NDR-75 output 75W / eff 0.88 | 85 VA in
PSU4 (F19) | 60 | NDR-240 at rail-B share ~50W / eff 0.9 | 56 VA in
L1 TOTAL | 141 | vs 250 VA half-winding | 56% - PASS
Leg L2 (CTRL_L2)
PSU2 (F7) | 75 |  | 85 VA
PSU3 (F9) | 60 |  | 56 VA
L2 TOTAL | 141 | vs 250 VA | 56% - PASS
Dedicated fire branch (CB9, off SEC_L1 winding)
FACP1 + PSN1 standby | 30 | 0.25A @120V | battery recharge worst-case +48VA
FACP alarm + recharge case | 96 | 0.8A @120V | L1 winding total w/ fire branch = 237VA / 250VA = 95% - PASS, no margin for A/C
NOTE | 0 | Enclosure A/C + heater are NOT on T2 (REV K R-03) - fed from 380Y aux via CB10/CB11 | This is what keeps T2 at 500VA
FACP alarm case is transient (battery recharge current-limited). If a future load is added to either leg,
re-run this census; 1000 VA CPT is the documented upgrade path. [PE TO CONFIRM]

## NFPA72-W1
NFPA 72 SECONDARY SUPPLY WORKSHEET NFPA72-W1 (REV K, board finding R-16)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
Item | Current | Duration | Result
FACP1 (ARC-100 + CA-6075)
Standby current | 0.15045 A | x 24 h | 3.611 Ah
Alarm current (NAC + SLC + relays) | 3.9625 A | x 5 min | 0.330 Ah
Subtotal |  |  | 3.941 Ah
x1.2 derating (NFPA 72 10.6.7.2.1) |  |  | 4.73 Ah REQUIRED
Installed (BAT1/2) | 2x 12V 8Ah series |  | 8.0 Ah - PASS at 5-min term
OPEN TERM QUESTION | CATL manual306:809 cites 2 h sound+light | 24h + 2h case | 13.8 Ah - would FAIL; resolve term with AHJ at IFC (NEC 110.3(B) argues CATL governs)
PSN1 (separate calc - REV K)
Standby | 0.070 A [CONFIRM] | x 24 h | 1.68 Ah
Alarm (3 releasing ckts) | 3.4125 A | x 5 min | 0.284 Ah
x1.2 |  |  | 2.36 Ah REQUIRED
Installed (BAT3/4) | 2x 12V 8Ah series |  | 8.0 Ah - PASS
This single worksheet is the referenced source for drawing, BOM and handbook battery figures - the
3.3 Ah figure previously on sheet 7 was WRONG (31% low) and is superseded. Sign-off: fire alarm designer + AHJ.

## SCCR-HEAT
SCCR INPUTS + ENCLOSURE HEAT BALANCE INPUTS (REV K)
Z1SL-SCH-001 REV K ¦ z1Power - Sugarland BESS - EMS+MBMU panel ¦ PROPRIETARY - STR MEDICAL ¦ FOR REVIEW ONLY - NOT FOR CONSTRUCTION - PE REVIEW REQUIRED ¦ 2026-08-09
Item | Value / basis | Notes
SCCR (UL 508A SB4) - inputs collected, worksheet by panel shop
Weakest expected component | DIN breakers 10kA (SU200M series proposed) | panel SCCR likely 10kA unless series-rated
Required | Utility available fault current at 480V POI (EOR study) | mark per 409.110(4) + 409.22(B)
Heat balance - inputs (full calc at IFC per selected A/C)
Internal dissipation | PSU1-4 ~35W + UPS 5W + CPUs 20W + SW 12W + MBMU/EM 25W + FACP/PSN 15W + misc 20W = ~132W | at 49C FACP ambient limit
Solar gain | 72x48x24 enclosure, worst face SW, absorptivity 0.65 | range 290-780W by shading - SITE DECISION
Design ambient | 36.7C (ASHRAE 0.4% Sugar Land TX) | A/C catalog capacity derate from L35/L35 required
Selected unit | ~1500 BTU/h (440W) 230V [SELECT AT IFC] | PASS only with shade structure OR up-size to 2500 BTU/h - decide with heat-balance calc
Neither sheet is complete without external inputs (utility fault current; site shading decision) - they are
structured here so the PE and panel shop fill blanks rather than reconstruct the analysis.