## BOM
Z1 SUGARLAND BESS - COMBINED EMS+MBMU ENCLOSURE - PANEL BILL OF MATERIALS
Rev K (PE review-board remediation incorporated) ¦ 2026-08-09 ¦ DWG Z1SL-E-001/A3-000 REV K ¦ BUDGETARY - NOT FOR PROCUREMENT ¦ Prices: 2026 USD street/list
Basis codes: QUOTED = live distributor price found 2026-08 ¦ EST = budgetary estimate +/-25% ¦ CATL = supplied with battery cabinets, $0 to panel ¦ TBD = pending ICD, carried as contingency
Blue cells are editable inputs (quantities, contingency %). All extended costs and totals are formulas.
Item | Ref Des | Description | Manufacturer | Part Number | Qty | Unit Cost (USD) | Ext Cost (USD) | Basis | Notes / Source
SHEET 2 - 480V POWER DISTRIBUTION
1 | Q1 | Main disconnect breaker 40A 3P UL489 DIN, 480V, marked IR | Phoenix Contact | TMC S3D (per Carson) [VERIFY AIC vs SCCR study] | 1 | 118 |  | EST | Carson carryover P/N; frame + AIC into SCCR worksheet Z1SL-SCH-001
2 | CB1 | SPD breaker 30A 3P UL489 DIN, 480Y/277V, 10kA min | ABB | SU203M-K30 [PROPOSED - CONFIRM AT PROCUREMENT] | 1 | 96 |  | EST | Per SPD mfr instruction; voltage + IR marked per REV K R-04
3 | SPD1 | Type 2 SPD, 480/277Y, NEMA panel mount | Raycap/Eaton | [VERIFY P/N + In/AIC] | 1 | 460 |  | EST | Good-practice addition; status indicator visible through window
4 | F1-F3 | Fuse, Class CC fast-acting 1A (meter taps) | Littelfuse | KLKR-1 | 3 | 9.2 |  | EST | Fuse schedule Z1SL-SCH-001
5 | F4,F5 | Fuse, Class CC TIME-DELAY 3A (CPT primary, 450.3(B) <=3A) | Littelfuse | FNQ-R-3 | 2 | 11.4 |  | EST | REV K R-05: KLKR fast-acting will not hold CPT inrush; <=3A per NEC 450.3(B) primary-only
6 | PT1 | Potential transformer set, 480:120, metering class | Functional Devices/ITI | [VERIFY ratio per Carson] | 1 | 430 |  | EST | Meter voltage reference
7 | TB1,TB13 | Feed-through TB, UT 6 (grey) + UT 6-PE (gn/ye) | Phoenix Contact | UT 6 / UT 6-PE | 12 | 3.4 |  | EST | 480V entry + 380Y aux feeder in; qty incl spares
8 | GB1 | Ground bus bar kit + lugs | Ilsco/Panduit | IGB-14 class [PROPOSED] | 1 | 48 |  | EST
Subtotal - SHEET 2 - 480V POWER DISTRIBUTION
SHEET 3 - CONTROL POWER + 24VDC (REV K RESTRUCTURE)
9 | T2 | Control power TX 500VA 480>120/240, encapsulated | SolaHD/HPS | E500 class [VERIFY] | 1 | 285 |  | EST | Per-leg VA census in Z1SL-SCH-001 (REV K R-03/R-62)
10 | CB2 | Control main breaker 2P 15A UL489 DIN, 240V, 10kA | ABB | SU202M-C15 [PROPOSED] | 1 | 72 |  | EST | Single-point 120V isolation
11 | CB9 | FIRE ALARM branch breaker 1P 15A UL489, RED handle + lock-on | ABB | SU201M-C15 + S2C-H6R red + MSL-2 lock [PROPOSED] | 1 | 88 |  | EST | REV K R-02: NEC 760.121(B) dedicated branch, feeds FACP1 + PSN1 only; placard at FACP
12 | F6,F7 | Fuse, Class CC time-delay 4A (PSU1/PSU2 primaries) | Littelfuse | CCMR-4 | 2 | 10.8 |  | EST | REV K R-05: time-delay for SMPS inrush
13 | F9,F19 | Fuse, Class CC time-delay 6A (PSU3/PSU4 primaries) | Littelfuse | CCMR-6 | 2 | 10.8 |  | EST
14 | F10-F18 | Fuse, Class CC: KLKR-2 x7 (CPU1/2, BMS1-3, IO, ETH), KLKR-3 x1 (network), KLKR-1 x1 (fire trip loop) | Littelfuse | KLKR-1/-2/-3 per schedule | 9 | 9.2 |  | EST | Ratings per fuse schedule Z1SL-SCH-001 (REV K R-05: every fuse now carries its ampere rating on the drawing)
15 |  | Fuse holder, Class CC, DIN | Altech | 2540104 (per Carson) | 18 | 12.5 |  | EST | One per fuse F1-F19 (18 total); labels 1:BMS1 2:BMS2 3:BMS3 4:IO 5:ETH per Carson
16 | PSU1,PSU2 | PSU 24VDC 75W DIN (rail A) | Mean Well | NDR-75-24 | 2 | 46 |  | EST | Redundant via RM1; ~35% loaded each
17 | PSU3,PSU4 | PSU 24VDC 240W/10A DIN (rail B, REV K R-08: now REDUNDANT pair) | Mean Well | NDR-240-24 | 2 | 88 |  | EST | REV K: PSU4 added - single-supply failure can no longer drop MBMU/ETH telemetry
18 | RM1 | Redundancy module 20A + DC-OK contact | Mean Well | DRDN20-24 [CONFIRM DC-OK contact option] | 1 | 54 |  | EST | DC-OK to IO1 DI3 (REV K R-09)
19 | RM2 | Redundancy module 40A + DC-OK contact (REV K) | Mean Well | DRDN40-24 [CONFIRM DC-OK contact option] | 1 | 78 |  | EST | PSU3+PSU4 ORing; DC-OK to IO1 DI4
20 | UPS1 | DC UPS supercap 4kJ 24VDC + signaling contact | Phoenix Contact | QUINT4-CAP/24DC/5/4KJ | 1 | 499.8 |  | QUOTED | Octopart 2026-08; buffer contact to IO1 DI5 (REV K R-09)
21 | K1 | Interposing relay, 2 Form C, 24VDC coil, DIN (PCS fire trip) | Phoenix Contact | RIF-1-RPT-LDP-24DC [PROPOSED] | 1 | 34 |  | EST | REV K R-01: normally-energized; dry contacts to Kehua EPO via X23
22 | BD1 | N-G bond kit #8 AWG Cu + lugs + label | Ilsco | [kit per shop practice] | 1 | 9 |  | EST | NEC 250.30 at CPT - the ONLY panel-side bond
Subtotal - SHEET 3 - CONTROL POWER + 24VDC (REV K RESTRUCTURE)
SHEET 4 - AUX DISTRIBUTION + ENCLOSURE CLIMATE (REV K)
23 | Q2 | Aux main breaker 25A 3P, 480Y/277V UL489, marked IR | ABB | SU203M-C25 [PROPOSED] | 1 | 96 |  | EST | UL508A incoming disconnect for 380Y feeder
24 | CB3,CB5,CB7 | Branch breaker 20A 1P UL489, C-curve, 480Y/277V, 10kA | ABB | SU201M-C20 [PROPOSED - REV K R-04] | 3 | 42 |  | EST | 380V L-L clearing duty per NEC 240.85; final value pends CATL RLA/MCA at RFI-002 (Art. 440)
25 | CB4,CB6,CB8 | Branch breaker 6A 1P UL489, C-curve, 480Y/277V, 10kA | ABB | SU201M-C6 [PROPOSED - REV K R-04] | 3 | 42 |  | EST | CATL BMS: 135W/2.3A, 6A <1s inrush
26 | CB10 | Enclosure A/C breaker 10A 1P UL489, 480Y/277V, lockable | ABB | SU201M-C10 + MSL-2 [PROPOSED] | 1 | 48 |  | EST | REV K R-03: NEC 440.14 disconnect = this breaker; final per unit MCA/MOCP
27 | CB11 | Enclosure heater breaker 6A 1P UL489, 480Y/277V | ABB | SU201M-C6 [PROPOSED] | 1 | 42 |  | EST | REV K R-03
28 | AC1 | Enclosure A/C, 230V, ~1500 BTU/h [final per heat balance] | Pfannenberg/nVent | DTS 3141 230V class [SELECT AT IFC] | 1 | 1480 |  | EST | REV K R-03: now a REAL circuit (CB10); heat-balance sheet governs final size
29 | HTR1,TH1 | Anti-condensation heater 100W + NC thermostat | Stego | HGL 046 + KTO 011 [PROPOSED] | 1 | 135 |  | EST | REV K R-03: now a real circuit (CB11/TH1)
30 |  | Warning label set per LABEL SCHEDULE Z1SL-SCH-001 (409.110 nameplate, 409.22(B), 110.16 arc flash, TWO SOURCES, FIRE ALARM CIRCUIT, ESS signage) | - | - | 1 | 95 |  | EST | REV K R-17: full schedule replaces ad-hoc labels
31 | TB2-TB4 | Feed-through TB, UT 6 + UT 6-PE, cabinet aux circuits | Phoenix Contact | UT 6 / UT 6-PE | 15 | 3.4 |  | EST | HVAC L/N + BMS L/N + PE per cabinet
Subtotal - SHEET 4 - AUX DISTRIBUTION + ENCLOSURE CLIMATE (REV K)
SHEET 5 - EMS + NETWORKING
32 | CPU1,CPU2 | EMS computer, Arm DIN-rail, Linux (Battalion image) | Moxa | UC-2222A-T-US | 2 | 854.26 |  | QUOTED | shopmoxa.neteon.net 2026-08 (backorder - check lead time)
33 | SW1 | Managed switch 14-port, VLAN, DIN | Moxa | EDS-4014 [VERIFY variant w/ Battalion] | 1 | 790 |  | EST | VLAN 10/20/30 config sheet in Z1SL-SCH-001
34 | IO1 | Remote I/O, 6 DI / 6 relay DO, Ethernet | Moxa | ioLogik E1214 | 1 | 265 |  | EST | FACP ALM/SUP/TRB (N/C, REV K) + RM1/RM2/UPS1 health (REV K R-09)
35 |  | Cat 6A shielded patch cords, assorted 0.5-3m | Panduit or equal | - | 14 | 11 |  | EST | Cat 6A per CATL spec; one SKU panel-wide
Subtotal - SHEET 5 - EMS + NETWORKING
SHEET 6 - MBMU + CAN
36 | MBMU1-3 | Master BMS unit | CATL | - | 3 | 0 |  | CATL | Supplied with EnerOne+ cabinets - $0 to panel BOM
37 | EM1-3 | ETH comms module | CATL | - | 3 | 0 |  | CATL | Supplied with cabinets
38 | R1-R3 | Termination resistor 60R 0.25W - crimped into MBMU J5.33/34 | - | - | 3 | 0.8 |  | EST | CARSON AS-BUILT. Commission check: J902.21/22 ~60R expected; if ~30R remove (over-termination). ICD item
39 | TB5-TB7 | TB, UK 5 N insulated feed-through (CAN H/L) | Phoenix Contact | UK 5 N | 6 | 1.8 |  | EST | REV J FIX retained: not USLKG ground blocks
40 | SB1-SB3 | TB, USLKG 5 ground block - CAN SHIELD POLES ONLY | Phoenix Contact | USLKG 5 | 3 | 2.9 |  | EST | Single-point shield ground, one per cabinet, in netlist
41 |  | Crimp contact, MX34 0.5mm2 signal (CAN/COMM/24V) | JAE | M34S75C4F2 | 60 | 0.35 |  | EST | REV K R-44: MX34JAHL connector system is JAE (was mis-attributed Molex); qty incl spares
42 |  | Crimp contact, MX34 CAN-shield DEDICATED | JAE | M34S75C4F3 | 12 | 0.4 |  | EST | Shield uses its own contact type per CATL SOP
43 |  | Connector plugs J5/J3/J902 (360242-00175/-00136/-00078) + JX1/JX2 (-00813/-00814) | CATL/Recodeal | - | 0 | 0 |  | CATL | Normally supplied with cabinets - VERIFY at order (REV K R-45: CATL scope, not panel scope)
44 |  | AWG10 JONHON aux adapter cables at JXH1 (plug 360242-00760) | CATL | - | 0 | 0 |  | CATL | A/B chiller, C/D BMS; supplied w/ cabinet - VERIFY (CATL scope)
Subtotal - SHEET 6 - MBMU + CAN
SHEETS 7+9 - FIRE ALARM + RELEASING (OPTION B, REV K)
45 | FACP1 | Addressable releasing FACP, 100-pt | Potter | ARC-100 | 1 | 1554 |  | QUOTED | firealarm.com 2026-08; relay 26/27 programmed normally-energized for PCS trip (REV K R-01)
46 | FACP1 | Class A SLC expansion card (installs in FACP1) | Potter | CA-6075 | 1 | 268 |  | EST | Class A loop: panel > cab1 > cab2 > cab3 > panel, rack-to-rack (REV K R-11)
47 | PSN1 | Listed releasing/aux power supply 10A (3A/ckt) | Potter | PSN-1000 | 1 | 640 |  | EST | REV K R-12: now a REAL component (was contingency) - 1.1375A/cab alarm load vs ARC-100 1A I/O rating; own battery + NFPA 72 calc
48 | BAT1,BAT2 | Battery 12V 8Ah SLA (FACP) | Power-Sonic | PS-1280 | 2 | 33 |  | EST | Worksheet NFPA72-W1: 4.73Ah req (24h + 5min); 2h CATL term with AHJ
49 | BAT3,BAT4 | Battery 12V 8Ah SLA (PSN1, REV K) | Power-Sonic | PS-1280 | 2 | 33 |  | EST | PSN-1000 separate secondary supply calc in NFPA72-W1
50 | DS1 | Releasing service disconnect, 3-ckt, lockable, position-supervised | Potter/equal | [CONFIRM LISTED DEVICE AT ICD] | 1 | 180 |  | EST | REV K R-15: maintenance disable for all three releasing circuits; monitored via MM1
51 | MM1-MM3 | SLC monitor module (DS1 position / PSN trouble / manual release) | Potter | PAD100-IM [CONFIRM] | 3 | 92 |  | EST | REV K: supervision of releasing-chain auxiliaries on the SLC
52 | SIR1 | Siren, 24VDC, panel mount | Potter | SQ-24 class [PROPOSED] | 1 | 68 |  | EST | Top left of enclosure per Carson
53 | STB1 | Strobe/horn | Eaton | HT8AEHA (per Carson) | 1 | 215 |  | EST
54 | X24 | Abort station, constant-pressure, guarded (FIELD at cabinet line-up) | Potter | APS-1 class [CONFIRM AT ICD] | 1 | 145 |  | EST | REV K R-14: NFPA 72 23.8.5.6 - located in protected area, supervised, abort-active indication
55 | X25 | Manual release station, dual-action (FIELD) | Potter | RMS-1T class [CONFIRM AT ICD] | 1 | 98 |  | EST | REV K R-15
56 | R4-R8,R10-R12 | EOL devices: NAC(R4), SUP1-3(R5-7), abort(R8), MM inputs(R10,R12), man-rel(R11) | Potter | EOLD 3005012 | 8 | 16 |  | EST | REV K R-13: every supervised circuit now has its EOL IN the netlist, installed at the far end
57 | TB8,TB9,TB14-16,TB23 | TB, UK 5 N insulated feed-through (SLC send/return, suppression, abort, man-rel, EPO) | Phoenix Contact | UK 5 N | 20 | 1.8 |  | EST | Feed-through only - never USLKG on supervised circuits; qty incl spares
Subtotal - SHEETS 7+9 - FIRE ALARM + RELEASING (OPTION B, REV K)
SHEET 8 - METERING
58 | M1 | Revenue meter, 15 CT inputs, Ethernet | eGauge | EG4115 (Core) | 1 | 850 |  | EST | SCOPE DEVIATION - client approval; confirm SKU/price
59 | X15-X17 | Split-core CT, 333mV UL2808 (PoI/Solar/BESS L1-L3, field sets) | eGauge | ECS series [size per conductor] | 9 | 96 |  | EST | Open-circuit safe - no shorting blocks required
60 | TB11 | TB, UT 4 feed-through (CT landing, 18 pos + spares) | Phoenix Contact | UT 4 | 20 | 2.6 |  | EST | REV K R-06: feed-through UT 4 - NOT USLKG (A3 sheet 8 value corrected)
Subtotal - SHEET 8 - METERING
ENCLOSURE + HARDWARE
61 |  | NEMA 4 enclosure ~72x48x24, backplate + swing panel | Hoffman/Saginaw | [size per final layout sheet] | 1 | 4300 |  | EST | Layout/elevation sheet in Z1SL-SCH-001 (working space, 760.136 segregation, bending space)
62 |  | DIN rail, wire duct, panel hardware | - | - | 1 | 290 |  | EST
63 |  | Panel wire: MTW/THHN, FPL (fire), AWG20 CAN pair, Cat 6A bulk, ferrules, labels | - | - | 1 | 760 |  | EST | Wire numbers assigned at fab release
Subtotal - ENCLOSURE + HARDWARE
FIELD EQUIPMENT (PANEL-ADJACENT SCOPE - BY OTHERS)
64 | X18 | Aux 380Y/220V source = Kehua PCS Cabinet-375 internal 30kVA 480/380 TX + 3 output breakers | Kehua | - | 0 | 0 |  | KEHUA | Kehua scope (REV I); breaker ratings + N-G bond at RFI-001
65 |  | Aux feeder + EPO + fire-circuit field conduit & wire, panel > PCS/cabinets | - | - | 0 | 0 |  | EST | BY OTHERS / site contractor - excluded from panel BOM (REV K R-45 scope split)
Subtotal - FIELD EQUIPMENT (PANEL-ADJACENT SCOPE - BY OTHERS)
PARTS SUBTOTAL (all sections)
|  | Contingency % (budgetary pricing risk - editable) |  |  |  | 15%
BUDGETARY TOTAL - PANEL PARTS + PAD TX (excl. labor, engineering, freight, tax)
EXCLUSIONS: panel shop labor + UL508A listing fee (typ $8-15k this size), PE engineering/stamp, freight, tax,
site installation, CATL cabinets/PCS/PV (owner-furnished major equipment), TX pad + field conduit/wire (by others).
All EST prices are 2026 USD budgetary +/-25%. QUOTED prices are single-source web prices found 2026-08 and
expire immediately - obtain formal distributor quotes at procurement. TBD line (PSN-1000) resolves with CATL/Potter ICD.
Sources: shopmoxa.neteon.net (UC-2222A $854.26), firealarm.com (ARC-100 $1,554.00), Octopart (QUINT4-CAP 4KJ $499.80),
store.egauge.net (Core EG4015-64E $833.38). CATL aux load data: EnerOne+ public spec (7SUN distributor copy).
DEVIATIONS PENDING CLIENT APPROVAL: single eGauge meter; external pad TX; single managed switch (see Rev D root sheet).